## Slide 1: Fuel Cell Application
Notes: The lightfoat is located just off the coast of Liverpool.
Only solar power, but was designed to have a potable generator “plugged in” to charge the batteries

## Slide 2: The problem – old batteries
2012 / 13 - Intervention with Diesel Alternators
Notes: This is an analogue trend of the main battery voltage from our monitoring system.
The existing batteries on the lightfloat were getting old and not how sufficient power to get through the winter.
Approximately 60% of the capacity has been used by the time the voltage reaches 24v
The systems are designed such that if all is healthy then this should not occur.
By the beginning to mid Nov, we were at this point.
Intervention was then required to lift on a generator and change the batteries.
This proves both difficult, due to weather condition, costly, due to relocating a ship and is not effective as it requires extended running of a portable generator.
But we get through the winter.

## Slide 3: The requirement
Avoid fitting a diesel generator
Reliable source of power
Retro fit at sea
Extended running without intervention or refuelling
Notes: Eliminate the need for a generator to be temporarily installed
Must be reliable such that there are not return visits, incurring extra ship time
Equipment needs to be light and portable, allowing fitting at sea
Needs to be able to run throughout the winter period

## Slide 4: The concept
Use of a small fuel cell (110W max)
Charging starts at 24v
Charging of batteries for about 6 hours daily (approx. 0.7kW)
The goal it to maintain the status but not to recharge.
Enough fuel for about 90 day operation
Notes: Use of a small fuel cell that can meet the daily load demand i.e. replace the energy taken from the batteries each day, but no more. For this station it was typically 0.7kWh or 29Ah per day @24v
The goal is to maintain the batteries rather than recover them.
Charging starts when the batteries are at 24v or approx. 50 to 60% discharged.
90 days of operation should provide enough charging duration that the installed solar system power will start to recover the batteries.

## Slide 5: The application
Solar Regulator
Battery Fuse Protection
Fuel
Methanol at 0.9l per kWh
By-products
Water = 0.9l per kWh
Heat = Minimal
CO2 = 0.95kg/kWh
Load
Notes: Given that we will use about 0.7l of methanol a day and that there is 100l this should last 150 days
This system needed to be integrated into existing systems on site.
The heat, CO2 and water needed to be managed.
Heat was not an issue as this was insignificant into the cold hull of the lightfloat
CO2 was not an issue as the chosen location on the lightfloat was already vented.
This left the water that would need to be captured and stored

## Slide 6: A fuel cell stack
Notes: A Proton Exchange Membrane (PEM) for the Direct Methanol Fuel Cell.
Each membrane produces about 0.7v , so these are stacked together to get the desired voltage.

## Slide 7: The application
Notes: The solution was achieved using 4x25l containers of methanol.
A tank to capture the water
With the fuel cell fitted inside a Pelicase mounted on top of wooden and aluminum structure that could be manhandles and assembled into position.

## Slide 8: The Performance
Fuel Cell Fitted
Fuel Cell operation changed
Fuel Cell turned off
Notes: A trend of the main battery voltage from out monitoring system, but this time with the fuel cell in operation
Once fitted and after a couple of weeks running each day for about 6 hours, it was felt that we should increase the run time to about 10 hours. This allowed the batteries to be held in a slightly healthier state.
By about mid Feb, the solar gains start to pickup and the fuel cell is turned off.
The main battery system then recovers slowly using the available solar power.

## Slide 9: The Outcome
Fuel cell ran for about 60 days
About 60% of the Methanol was use
AtoN operation maintained
No additional unplanned visits